## CE Work Orders
Work Order # | CE Work Order # | Installation | Facility Number | Facility Name | Room/Area | Request DateTime | Requesting Organization | Work Category | Trade | Priority Code | Problem Description | Requested Action | Mission Impact | Status | Assigned Shop | Actions Taken | Completion Date
USSPC-FAC-2026-0001 | TRIRIGA-26-12001 | Peterson SFB | 3 | Power Generation Facility 3 | Control Room | 2026-02-01 0310Z | USSPACECOM J6 | Urgent | Fire Protection | 3 | Sprinkler head obstructed by stored materials in equipment room. | Clear obstructions from sprinkler head coverage area. | Yes – affects missile warning operations continuity. | In Progress | CE Fire Protection
USSPC-FAC-2026-0002 | TRIRIGA-26-12002 | Peterson SFB | 198 | Operations Building 198 | Lobby | 2026-02-01 0715Z | USSPACECOM J6 | Routine | ESS | 3 | CCTV camera 31 offline; no video feed to security monitoring. | Troubleshoot camera fault and restore video feed. | Yes – supports satellite command and control systems. | Completed | CE ESS | Technician inspected ESS components. Identified controller firmware communication error. Replaced network cable and verified video feed. System tested end-to-end; all access points verified operational. Security notified of restoration. | 2026-02-16
USSPC-FAC-2026-0003 | TRIRIGA-26-12003 | Buckley SFB | 180 | Mission Support Facility 180 | Mechanical Room | 2026-02-01 0905Z | USSPACECOM J6 | Emergency | Plumbing | 2 | Water hammer occurring in supply piping when fixtures cycle. | Install water hammer arrestors and secure piping supports. | Yes – impacts secure communications capability. | Completed | CE Plumbing | Technician inspected and identified Found corroded pipe fitting at joint. Replaced pressure regulator and set to 55 PSI. System pressure tested and verified at normal operating range. No further leaks observed. | 2026-02-03
USSPC-FAC-2026-0004 | TRIRIGA-26-12004 | Schriever SFB | 155 | Operations Building 155 | Raised Floor Area | 2026-02-01 1310Z | USSPACECOM J2 | Urgent | Lighting | 2 | Parking lot light pole 19 dark; ballast or photocell suspected. | Replace ballast or photocell and restore pole light operation. | Potential – potential cascade failure if not addressed. | Submitted | CE Lighting
USSPC-FAC-2026-0005 | TRIRIGA-26-12005 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-01 1405Z | USSPACECOM J3 | Routine | Fire Protection | 4 | Fire alarm notification appliances inaudible in high-ambient-noise areas. | Adjust notification appliance output or add devices for coverage. | No – general facility maintenance. | Submitted | CE Fire Protection
USSPC-FAC-2026-0006 | TRIRIGA-26-12006 | Schriever SFB | 220 | Mission Support Building 220 | Mechanical Room | 2026-02-01 1435Z | USSPACECOM J6 | Routine | HVAC | 4 | Compressor on chiller 4 showing end-of-life indicators; elevated discharge pressure. | Evaluate compressor condition; repair or replace as needed. | No – aesthetic/comfort issue only. | Completed | CE HVAC | Technician responded and found Found dirty evaporator coil restricting airflow. Repaired leak, evacuated, and recharged to nameplate specification. System tested and verified operational at 88°F. All work per UFC 3-410-01. | 2026-02-12
USSPC-FAC-2026-0007 | TRIRIGA-26-12007 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-01 1515Z | USSPACECOM J4 | Preventive Maintenance | Electrical | 4 | Automatic transfer switch failed to transfer during scheduled test. | Perform thermographic survey and document findings. | No – preventive maintenance. | Scheduled | CE Electrical
USSPC-FAC-2026-0008 | TRIRIGA-26-12008 | Vandenberg SFB | 77 | Secure Data Facility 77 | Server Room B | 2026-02-01 1625Z | USSPACECOM J4 | Urgent | Lighting | 2 | Exterior security lighting inoperative on building north side. | Repair exterior security lighting and verify coverage. | Yes – delayed access to mission operations spaces. | Approved | CE Lighting
USSPC-FAC-2026-0009 | TRIRIGA-26-12009 | Buckley SFB | 312 | Operations Annex 312 | Server Closet | 2026-02-01 1705Z | USSPACECOM J2 | Urgent | Electrical | 3 | Voltage sag measured at distribution panel; equipment brownouts reported. | Investigate voltage sag source and correct distribution issue. | Yes – supports satellite uplink equipment. | Completed | CE Electrical | Technician de-energized and inspected per NFPA 70E. Found ATS control board fault. Replaced failed battery cells and load tested string. System re-energized and tested under load; operating normally. | 2026-02-03
USSPC-FAC-2026-0010 | TRIRIGA-26-12010 | Schriever SFB | 220 | Mission Support Building 220 | Electrical Closet | 2026-02-01 1845Z | USSPACECOM J4 | Emergency | Structural | 1 | Overhead coiling door not tracking properly; binding intermittently. | Adjust door tracks and lubricate guide system. | Yes – delayed access to mission operations spaces. | Approved | CE Structural
USSPC-FAC-2026-0011 | TRIRIGA-26-12011 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-01 1910Z | USSPACECOM J3 | Urgent | Fire Protection | 3 | Emergency exit sign non-illuminated in corridor section. | Replace emergency exit sign lamps and verify illumination. | Yes – degrades mission operations center readiness. | In Progress | CE Fire Protection
USSPC-FAC-2026-0012 | TRIRIGA-26-12012 | Vandenberg SFB | 51 | Launch Operations Building 51 | Electrical Room | 2026-02-01 2010Z | USSPACECOM J4 | Urgent | Power Production | 3 | Generator exhaust leak detected at flexible coupling. | Repair exhaust leak and verify emissions containment. | Yes – degrades ground station equipment reliability. | In Progress | CE Power Production
USSPC-FAC-2026-0013 | TRIRIGA-26-12013 | Vandenberg SFB | 51 | Launch Operations Building 51 | Electrical Room | 2026-02-01 2155Z | USSPACECOM J4 | Routine | Plumbing | 4 | Hot water temperature at fixtures below acceptable range; measured 91°F. | Diagnose hot water temperature issue and adjust or repair. | No – routine upkeep; no operational impact. | Approved | CE Plumbing
USSPC-FAC-2026-0014 | TRIRIGA-26-12014 | Vandenberg SFB | 134 | Range Control Facility 134 | Mechanical Room | 2026-02-01 2255Z | USSPACECOM J2 | Urgent | ESS | 2 | CCTV camera 25 offline; no video feed to security monitoring. | Troubleshoot camera fault and restore video feed. | Yes – delayed access to mission operations spaces. | In Progress | CE ESS
USSPC-FAC-2026-0015 | TRIRIGA-26-12015 | Schriever SFB | 400 | Satellite Operations Facility 400 | Ground Station Control Room | 2026-02-01 2325Z | USSPACECOM J2 | Routine | HVAC | 3 | Thermostat in zone 6 non-responsive; unable to maintain setpoint. | Replace thermostat and verify zone control operation. | No – personnel safety concern. | In Progress | CE HVAC
USSPC-FAC-2026-0016 | TRIRIGA-26-12016 | Peterson SFB | 198 | Operations Building 198 | Electrical Room | 2026-02-01 2345Z | USSPACECOM J6 | Emergency | Plumbing | 2 | Isolation valve on chilled water loop will not fully close; stem corroded. | Replace isolation valve and verify system integrity. | Yes – impacts real-time telemetry processing. | Completed | CE Plumbing | Technician inspected and identified Found corroded pipe fitting at joint. Filled trap and installed trap primer. System pressure tested and verified at normal operating range. No further leaks observed. | 2026-02-03
USSPC-FAC-2026-0017 | TRIRIGA-26-12017 | Buckley SFB | 180 | Mission Support Facility 180 | Exterior Pad | 2026-02-02 0220Z | USSPACECOM J3 | Routine | Fire Protection | 4 | Sprinkler head obstructed by stored materials in equipment room. | Clear obstructions from sprinkler head coverage area. | Potential – could impact mission systems if leak reaches equipment. | In Progress | CE Fire Protection
USSPC-FAC-2026-0018 | TRIRIGA-26-12018 | Schriever SFB | 302 | Communications Facility 302 | Electrical Room | 2026-02-02 0310Z | USSPACECOM J3 | Urgent | Lighting | 2 | LED retrofit fixture failed prematurely; driver humming audible. | Replace failed LED driver and fixture. | Potential – risk to nearby equipment if condition worsens. | Submitted | CE Lighting
USSPC-FAC-2026-0019 | TRIRIGA-26-12019 | Peterson SFB | 198 | Operations Building 198 | Roof | 2026-02-02 0840Z | USSPACECOM J3 | Emergency | HVAC | 1 | Intermittent fault on CRAC unit 4; temperature cycling outside acceptable range. | Troubleshoot CRAC unit fault and restore environmental controls. | Yes – intermittent loss of operator consoles. | Completed | CE HVAC | Technician responded and found Identified refrigerant undercharge due to slow leak at service valve. Replaced VFD drive board and programmed to original parameters. System tested and verified operational at 83°F. All work per UFC 3-410-01. | 2026-02-02
USSPC-FAC-2026-0020 | TRIRIGA-26-12020 | Vandenberg SFB | 134 | Range Control Facility 134 | Mechanical Room | 2026-02-02 0925Z | USSPACECOM J6 | Urgent | Electrical | 3 | Conduit damage observed along exterior wall; wiring exposed to weather. | Repair conduit and reseal exterior penetration. | Yes – supports space domain awareness operations. | Submitted | CE Electrical
USSPC-FAC-2026-0021 | TRIRIGA-26-12021 | Vandenberg SFB | 134 | Range Control Facility 134 | Exterior HVAC Pad | 2026-02-02 1520Z | USSPACECOM J3 | Emergency | HVAC | 2 | Degraded airflow detected in underfloor plenum; hot spots forming near rack rows. | Investigate underfloor airflow restriction and restore cooling distribution. | Yes – supports satellite uplink equipment. | Approved | CE HVAC
USSPC-FAC-2026-0022 | TRIRIGA-26-12022 | Peterson SFB | 105 | Communications Hub 105 | Cable Vault | 2026-02-02 1540Z | USSPACECOM J3 | Urgent | Plumbing | 2 | Corrosion visible on exposed copper piping in mechanical chase. | Evaluate pipe corrosion and replace affected sections. | Yes – delayed access to mission operations spaces. | In Progress | CE Plumbing
USSPC-FAC-2026-0023 | TRIRIGA-26-12023 | Schriever SFB | 400 | Satellite Operations Facility 400 | Ground Station Control Room | 2026-02-02 1625Z | USSPACECOM J6 | Urgent | Plumbing | 3 | Water hammer occurring in supply piping when fixtures cycle. | Install water hammer arrestors and secure piping supports. | Potential – potential cascade failure if not addressed. | In Progress | CE Plumbing
USSPC-FAC-2026-0024 | TRIRIGA-26-12024 | Buckley SFB | 180 | Mission Support Facility 180 | Electrical Room | 2026-02-02 1735Z | USSPACECOM J3 | Emergency | ESS | 1 | Duress alarm button at post 1 non-functional during test. | Replace duress alarm switch and test signaling. | Yes – degrades ground station equipment reliability. | Approved | CE ESS
USSPC-FAC-2026-0025 | TRIRIGA-26-12025 | Schriever SFB | 220 | Mission Support Building 220 | Restroom Wing | 2026-02-02 1750Z | USSPACECOM J3 | Routine | Fire Protection | 4 | Fire pump failed to start during weekly test sequence. | Troubleshoot fire pump controller and restore start capability. | No – quality of life issue; no mission degradation. | Completed | CE Fire Protection | Technician inspected system per NFPA 72/25 requirements. Found fire pump controller relay failure. Replaced control module and reprogrammed zone. System placed back in service and tested. All zones normal. | 2026-02-08
USSPC-FAC-2026-0026 | TRIRIGA-26-12026 | Peterson SFB | 210 | Operations Building 210 | Ops Floor | 2026-02-02 1835Z | USSPACECOM J2 | Routine | ESS | 4 | Perimeter fence detection system reporting intermittent faults. | Troubleshoot perimeter detection system and restore monitoring. | No – aesthetic/comfort issue only. | Completed | CE ESS | Responded and coordinated with security forces. Identified controller firmware communication error. Replaced card reader assembly and programmed to system. Credentials tested at affected entry points; full functionality confirmed. | 2026-02-21
USSPC-FAC-2026-0027 | TRIRIGA-26-12027 | Vandenberg SFB | 51 | Launch Operations Building 51 | Electrical Room | 2026-02-02 1905Z | USSPACECOM J6 | Routine | Lighting | 4 | Flickering fluorescent fixtures in office area causing occupant complaints. | Replace flickering fixtures with new lamps or ballasts. | No – personnel safety and usability concern. | In Progress | CE Lighting
USSPC-FAC-2026-0028 | TRIRIGA-26-12028 | Buckley SFB | 312 | Operations Annex 312 | Electrical Room | 2026-02-02 2215Z | USSPACECOM J2 | Routine | HVAC | 4 | Refrigerant leak suspected on split system unit; ice formation on suction line. | Locate and repair refrigerant leak; recharge system to spec. | No – aesthetic/comfort issue only. | Completed | CE HVAC | Technician responded and found Discovered failed VFD drive board. Cleared drain, treated with biocide, and verified flow. System tested and verified operational at 90°F. All work per UFC 3-410-01. | 2026-02-21
USSPC-FAC-2026-0029 | TRIRIGA-26-12029 | Peterson SFB | 210 | Operations Building 210 | Loading Dock | 2026-02-02 2250Z | USSPACECOM J4 | Routine | Structural | 3 | Overhead coiling door not tracking properly; binding intermittently. | Adjust door tracks and lubricate guide system. | No – quality of life issue; no mission degradation. | Submitted | CE Structural
USSPC-FAC-2026-0030 | TRIRIGA-26-12030 | Vandenberg SFB | 134 | Range Control Facility 134 | Mechanical Room | 2026-02-02 2315Z | USSPACECOM J3 | Urgent | ESS | 3 | Electronic lock on secure door not responding to valid credentials. | Replace electronic lock actuator and verify operation. | Yes – impacts secure communications capability. | In Progress | CE ESS
USSPC-FAC-2026-0031 | TRIRIGA-26-12031 | Vandenberg SFB | 77 | Secure Data Facility 77 | Electrical Vault | 2026-02-03 0155Z | USSPACECOM J4 | Urgent | Lighting | 2 | Emergency lighting battery unit failed self-test; no backup illumination. | Replace emergency lighting battery unit and test. | Yes – intermittent loss of operator consoles. | In Progress | CE Lighting
USSPC-FAC-2026-0032 | TRIRIGA-26-12032 | Peterson SFB | 3 | Power Generation Facility 3 | Switchgear Room | 2026-02-03 0305Z | USSPACECOM J3 | Urgent | Electrical | 3 | Circuit breaker E-5 will not reset after trip; possible internal fault. | Replace faulty circuit breaker and verify proper operation. | Yes – intermittent loss of operator consoles. | In Progress | CE Electrical
USSPC-FAC-2026-0033 | TRIRIGA-26-12033 | Peterson SFB | 198 | Operations Building 198 | Loading Area | 2026-02-03 0340Z | USSPACECOM J6 | Urgent | Electrical | 3 | Voltage sag measured at distribution panel; equipment brownouts reported. | Investigate voltage sag source and correct distribution issue. | Yes – supports satellite uplink equipment. | Completed | CE Electrical | Responded to work order. Discovered deteriorated wire insulation in conduit. Replaced failed battery cells and load tested string. Thermal scan confirmed normal temperatures. Completed per NEC requirements. | 2026-02-08
USSPC-FAC-2026-0034 | TRIRIGA-26-12034 | Peterson SFB | 145 | Operations Building 145 | Restroom Corridor | 2026-02-03 0400Z | USSPACECOM J6 | Emergency | Electrical | 2 | Emergency power receptacle non-functional at designated location. | Repair or replace emergency power receptacle. | Yes – impacts secure communications capability. | In Progress | CE Electrical
USSPC-FAC-2026-0035 | TRIRIGA-26-12035 | Peterson SFB | 42 | Administrative Building 42 | Restroom A | 2026-02-03 0455Z | USSPACECOM J6 | Routine | Fire Protection | 4 | Fire alarm notification appliances inaudible in high-ambient-noise areas. | Adjust notification appliance output or add devices for coverage. | No – preventive maintenance. | In Progress | CE Fire Protection
USSPC-FAC-2026-0036 | TRIRIGA-26-12036 | Vandenberg SFB | 51 | Launch Operations Building 51 | Equipment Room | 2026-02-03 0730Z | USSPACECOM J6 | Preventive Maintenance | ESS | 4 | Preventive maintenance on access control system firmware and hardware. | Repair intercom system and test two-way communication. | No – preventive maintenance. | Completed | CE ESS | Technician inspected ESS components. Found door lock solenoid failure. Cleaned sensor lens and recalibrated detection zone. System tested end-to-end; all access points verified operational. Security notified of restoration. | 2026-02-15
USSPC-FAC-2026-0037 | TRIRIGA-26-12037 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-03 0810Z | USSPACECOM J4 | Urgent | Electrical | 3 | PDU in server room reporting overload alarm on Phase B. | Investigate PDU overload and redistribute loads as needed. | Yes – supports satellite uplink equipment. | In Progress | CE Electrical
USSPC-FAC-2026-0038 | TRIRIGA-26-12038 | Schriever SFB | 220 | Mission Support Building 220 | Corridor B | 2026-02-03 0835Z | USSPACECOM J2 | Emergency | Electrical | 1 | Frequent breaker trips observed on mission operations power panel E-8. | Inspect panel, identify overload condition, and replace faulty breakers. | Yes – affects missile warning operations continuity. | In Progress | CE Electrical
USSPC-FAC-2026-0039 | TRIRIGA-26-12039 | Buckley SFB | 312 | Operations Annex 312 | Rooftop | 2026-02-03 1050Z | USSPACECOM J3 | Routine | Fire Protection | 3 | Clean agent suppression system showing low bottle pressure. | Recharge or replace clean agent suppression bottles. | Yes – impacts secure communications capability. | Completed | CE Fire Protection | Responded and placed system in test mode. Found faulty smoke detector head. Replaced control module and reprogrammed zone. Fire alarm panel cleared; all devices verified operational. | 2026-02-19
USSPC-FAC-2026-0040 | TRIRIGA-26-12040 | Vandenberg SFB | 134 | Range Control Facility 134 | Telemetry Room | 2026-02-03 1415Z | USSPACECOM J6 | Urgent | HVAC | 2 | Degraded airflow detected in underfloor plenum; hot spots forming near rack rows. | Investigate underfloor airflow restriction and restore cooling distribution. | Yes – supports satellite uplink equipment. | Completed | CE HVAC | Arrived on-site, isolated unit, and performed diagnostic. Found clogged condensate drain line. Cleaned coil, replaced filters, and verified airflow. Post-repair monitoring confirmed stable operation. | 2026-02-08
USSPC-FAC-2026-0041 | TRIRIGA-26-12041 | Peterson SFB | 105 | Communications Hub 105 | Ground Floor Lobby | 2026-02-03 1610Z | USSPACECOM J3 | Preventive Maintenance | HVAC | 4 | Annual filter replacement and coil cleaning for AHU-3 through AHU-7. | Replace filters and clean coils on all air handling units. | No – preventive maintenance. | In Progress | CE HVAC
USSPC-FAC-2026-0042 | TRIRIGA-26-12042 | Schriever SFB | 302 | Communications Facility 302 | Mechanical Room | 2026-02-03 2020Z | USSPACECOM J4 | Routine | Electrical | 3 | Conduit damage observed along exterior wall; wiring exposed to weather. | Repair conduit and reseal exterior penetration. | No – routine upkeep; no operational impact. | In Progress | CE Electrical
USSPC-FAC-2026-0043 | TRIRIGA-26-12043 | Peterson SFB | 3 | Power Generation Facility 3 | Switchgear Room | 2026-02-03 2105Z | USSPACECOM J4 | Preventive Maintenance | HVAC | 4 | Preventive maintenance due on chiller plant per manufacturer interval. | Perform chiller preventive maintenance per manufacturer requirements. | No – preventive maintenance. | Scheduled | CE HVAC
USSPC-FAC-2026-0044 | TRIRIGA-26-12044 | Schriever SFB | 400 | Satellite Operations Facility 400 | Server Room | 2026-02-03 2250Z | USSPACECOM J3 | Routine | ESS | 4 | Perimeter fence detection system reporting intermittent faults. | Troubleshoot perimeter detection system and restore monitoring. | No – preventive maintenance. | Submitted | CE ESS
USSPC-FAC-2026-0045 | TRIRIGA-26-12045 | Vandenberg SFB | 134 | Range Control Facility 134 | Mechanical Room | 2026-02-04 0210Z | USSPACECOM J3 | Urgent | HVAC | 2 | Cooling tower fan motor tripped on overload; condenser water temperature rising. | Repair cooling tower fan motor and test operation. | Yes – intermittent loss of operator consoles. | Submitted | CE HVAC
USSPC-FAC-2026-0046 | TRIRIGA-26-12046 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-04 0440Z | USSPACECOM J6 | Routine | Electrical | 4 | Electrical panel cover missing fasteners; exposed energized components. | Secure panel cover and replace missing fasteners. | No – quality of life issue; no mission degradation. | Submitted | CE Electrical
USSPC-FAC-2026-0047 | TRIRIGA-26-12047 | Schriever SFB | 302 | Communications Facility 302 | Roof | 2026-02-04 0635Z | USSPACECOM J4 | Routine | HVAC | 3 | Thermostat in zone 9 non-responsive; unable to maintain setpoint. | Replace thermostat and verify zone control operation. | Potential – risk to nearby equipment if condition worsens. | Completed | CE HVAC | Inspected system per work order. Identified refrigerant undercharge due to slow leak at service valve. Replaced VFD drive board and programmed to original parameters. Verified airflow and temperature within acceptable parameters. Documentation submitted. | 2026-02-22
USSPC-FAC-2026-0048 | TRIRIGA-26-12048 | Peterson SFB | 145 | Operations Building 145 | Entry Vestibule | 2026-02-04 0655Z | USSPACECOM J2 | Urgent | Structural | 3 | Ceiling tile damage from water intrusion; multiple tiles sagging. | Replace damaged ceiling tiles and identify water source. | No – personnel safety concern. | Approved | CE Structural
USSPC-FAC-2026-0049 | TRIRIGA-26-12049 | Peterson SFB | 42 | Administrative Building 42 | Parking Structure | 2026-02-04 0715Z | USSPACECOM J2 | Routine | HVAC | 4 | Cooling unit shut down unexpectedly; room temperature rising steadily. | Restore HVAC operation and verify system stability. | No – aesthetic/comfort issue only. | Submitted | CE HVAC
USSPC-FAC-2026-0050 | TRIRIGA-26-12050 | Peterson SFB | 3 | Power Generation Facility 3 | Generator Bay 2 | 2026-02-04 1225Z | USSPACECOM J4 | Emergency | HVAC | 2 | Return air temperature sensor reading erratic values; zone control degraded. | Replace return air temperature sensor and recalibrate. | Yes – impacts secure communications capability. | Completed | CE HVAC | Technician responded and found Found BAS controller communication card fault. Replaced capacitor and verified compressor amp draw within spec. System tested and verified operational at 93°F. All work per UFC 3-410-01. | 2026-02-04
USSPC-FAC-2026-0051 | TRIRIGA-26-12051 | Schriever SFB | 155 | Operations Building 155 | Electrical Room 2 | 2026-02-04 1335Z | USSPACECOM J2 | Routine | Electrical | 4 | Ground fault detected on branch circuit serving critical equipment. | Locate and clear ground fault on branch circuit. | No – administrative area; no mission systems affected. | Submitted | CE Electrical
USSPC-FAC-2026-0052 | TRIRIGA-26-12052 | Schriever SFB | 400 | Satellite Operations Facility 400 | Antenna Maintenance Area | 2026-02-04 1345Z | USSPACECOM J4 | Emergency | Structural | 1 | Retaining wall showing lateral displacement; drainage weeps clogged. | Clear retaining wall weeps and assess lateral stability. | Yes – mission-critical data processing environment. | Completed | CE Structural | Technician assessed condition and documented findings. Identified moisture intrusion through failed sealant. Patched spalled area with structural repair mortar. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-04
USSPC-FAC-2026-0053 | TRIRIGA-26-12053 | Vandenberg SFB | 77 | Secure Data Facility 77 | Battery Room | 2026-02-04 1540Z | USSPACECOM J3 | Routine | Electrical | 3 | Ground fault detected on branch circuit serving critical equipment. | Locate and clear ground fault on branch circuit. | Yes – impacts real-time telemetry processing. | In Progress | CE Electrical
USSPC-FAC-2026-0054 | TRIRIGA-26-12054 | Peterson SFB | 198 | Operations Building 198 | Corridor B | 2026-02-04 1645Z | USSPACECOM J6 | Urgent | Electrical | 3 | Arc flash indicators detected during routine thermographic scan of switchgear. | De-energize and inspect switchgear; address arc flash indicators. | No – preventive maintenance. | Approved | CE Electrical
USSPC-FAC-2026-0055 | TRIRIGA-26-12055 | Vandenberg SFB | 134 | Range Control Facility 134 | Telemetry Room | 2026-02-04 1745Z | USSPACECOM J6 | Urgent | Fire Protection | 3 | Fire door held open with unauthorized wedge; closer mechanism degraded. | Repair fire door closer mechanism and verify self-closing. | Yes – delayed access to mission operations spaces. | Completed | CE Fire Protection | Responded and placed system in test mode. Identified low agent bottle pressure from slow leak. Replaced control module and reprogrammed zone. Fire alarm panel cleared; all devices verified operational. | 2026-02-05
USSPC-FAC-2026-0056 | TRIRIGA-26-12056 | Peterson SFB | 145 | Operations Building 145 | Mechanical Room | 2026-02-04 1830Z | USSPACECOM J4 | Preventive Maintenance | Electrical | 4 | Preventive maintenance due on UPS battery string per manufacturer schedule. | Inspect and test protective relays and breakers. | No – preventive maintenance. | Scheduled | CE Electrical
USSPC-FAC-2026-0057 | TRIRIGA-26-12057 | Vandenberg SFB | 134 | Range Control Facility 134 | Exterior HVAC Pad | 2026-02-04 1905Z | USSPACECOM J4 | Urgent | Structural | 2 | Floor tile cracked and lifting in high-traffic corridor; trip hazard. | Remove damaged floor tile and install replacement. | Yes – impacts secure communications capability. | Completed | CE Structural | Technician assessed condition and documented findings. Identified moisture intrusion through failed sealant. Applied new sealant and verified weathertight condition. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-09
USSPC-FAC-2026-0058 | TRIRIGA-26-12058 | Buckley SFB | 180 | Mission Support Facility 180 | Main Hall | 2026-02-04 2010Z | USSPACECOM J2 | Routine | Structural | 4 | Expansion joint sealant deteriorated on exterior wall; gap visible. | Remove and replace expansion joint sealant. | No – routine upkeep; no operational impact. | Approved | CE Structural
USSPC-FAC-2026-0059 | TRIRIGA-26-12059 | Peterson SFB | 3 | Power Generation Facility 3 | Generator Bay 1 | 2026-02-04 2305Z | USSPACECOM J2 | Routine | ESS | 4 | Perimeter fence detection system reporting intermittent faults. | Troubleshoot perimeter detection system and restore monitoring. | No – administrative area; no mission systems affected. | Approved | CE ESS
USSPC-FAC-2026-0060 | TRIRIGA-26-12060 | Peterson SFB | 145 | Operations Building 145 | Restroom Corridor | 2026-02-05 0435Z | USSPACECOM J3 | Urgent | Electrical | 2 | Neutral-to-ground voltage elevated at 2V; exceeding acceptable limits. | Investigate elevated neutral-to-ground voltage and correct. | Yes – intermittent loss of operator consoles. | Submitted | CE Electrical
USSPC-FAC-2026-0061 | TRIRIGA-26-12061 | Peterson SFB | 88 | Data Processing Facility 88 | Server Hall A | 2026-02-05 0610Z | USSPACECOM J4 | Routine | Electrical | 3 | Electrical panel cover missing fasteners; exposed energized components. | Secure panel cover and replace missing fasteners. | Potential – could impact mission systems if leak reaches equipment. | In Progress | CE Electrical
USSPC-FAC-2026-0062 | TRIRIGA-26-12062 | Buckley SFB | 180 | Mission Support Facility 180 | Mechanical Room | 2026-02-05 0620Z | USSPACECOM J4 | Preventive Maintenance | HVAC | 4 | Seasonal changeover inspection required for heating/cooling systems. | Inspect and repair air handling unit; restore cooling to acceptable range. | No – preventive maintenance. | Scheduled | CE HVAC
USSPC-FAC-2026-0063 | TRIRIGA-26-12063 | Schriever SFB | 400 | Satellite Operations Facility 400 | Antenna Maintenance Area | 2026-02-05 0850Z | USSPACECOM J4 | Routine | Lighting | 3 | Parking lot light pole 9 dark; ballast or photocell suspected. | Replace ballast or photocell and restore pole light operation. | Potential – risk to nearby equipment if condition worsens. | In Progress | CE Lighting
USSPC-FAC-2026-0064 | TRIRIGA-26-12064 | Peterson SFB | 88 | Data Processing Facility 88 | Receiving Area | 2026-02-05 0940Z | USSPACECOM J2 | Urgent | Lighting | 2 | High-bay lights in warehouse area cycling on and off intermittently. | Troubleshoot high-bay fixture cycling and correct. | No – general facility maintenance. | In Progress | CE Lighting
USSPC-FAC-2026-0065 | TRIRIGA-26-12065 | Peterson SFB | 105 | Communications Hub 105 | Ground Floor Lobby | 2026-02-05 1045Z | USSPACECOM J3 | Routine | ESS | 3 | Electronic lock on secure door not responding to valid credentials. | Replace electronic lock actuator and verify operation. | Yes – degrades mission operations center readiness. | Submitted | CE ESS
USSPC-FAC-2026-0066 | TRIRIGA-26-12066 | Peterson SFB | 42 | Administrative Building 42 | Parking Structure | 2026-02-05 1135Z | USSPACECOM J6 | Preventive Maintenance | HVAC | 4 | Seasonal changeover inspection required for heating/cooling systems. | Clear condensate drain and inspect for root cause of overflow. | No – preventive maintenance. | In Progress | CE HVAC
USSPC-FAC-2026-0067 | TRIRIGA-26-12067 | Buckley SFB | 312 | Operations Annex 312 | Rooftop | 2026-02-05 1220Z | USSPACECOM J4 | Routine | Electrical | 4 | Ground fault detected on branch circuit serving critical equipment. | Locate and clear ground fault on branch circuit. | No – personnel safety concern. | In Progress | CE Electrical
USSPC-FAC-2026-0068 | TRIRIGA-26-12068 | Schriever SFB | 155 | Operations Building 155 | UPS Room | 2026-02-05 1920Z | USSPACECOM J3 | Urgent | Electrical | 3 | Arc flash indicators detected during routine thermographic scan of switchgear. | De-energize and inspect switchgear; address arc flash indicators. | Yes – affects missile warning operations continuity. | In Progress | CE Electrical
USSPC-FAC-2026-0069 | TRIRIGA-26-12069 | Schriever SFB | 220 | Mission Support Building 220 | Electrical Closet | 2026-02-05 1940Z | USSPACECOM J3 | Preventive Maintenance | HVAC | 4 | Preventive maintenance due on chiller plant per manufacturer interval. | Inspect, clean, and document AHU condition. | No – preventive maintenance. | Approved | CE HVAC
USSPC-FAC-2026-0070 | TRIRIGA-26-12070 | Peterson SFB | 210 | Operations Building 210 | Electrical Room 1A | 2026-02-05 1940Z | USSPACECOM J2 | Urgent | Plumbing | 3 | Condensate drain line from AHU clogged; water collecting in drain pan. | Clear condensate drain line and treat to prevent recurrence. | Yes – degrades ground station equipment reliability. | Approved | CE Plumbing
USSPC-FAC-2026-0071 | TRIRIGA-26-12071 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-05 2020Z | USSPACECOM J6 | Emergency | Fire Protection | 1 | Fire alarm pull station damaged at egress point; device non-functional. | Replace damaged fire alarm pull station. | Yes – delayed access to mission operations spaces. | Completed | CE Fire Protection | Technician inspected system per NFPA 72/25 requirements. Found corroded alarm pull station contacts. Replaced control module and reprogrammed zone. System placed back in service and tested. All zones normal. | 2026-02-06
USSPC-FAC-2026-0072 | TRIRIGA-26-12072 | Vandenberg SFB | 51 | Launch Operations Building 51 | Roof | 2026-02-05 2025Z | USSPACECOM J3 | Urgent | Lighting | 3 | Exit sign lamp out at emergency egress route. | Replace exit sign lamp and verify illumination. | Potential – could impact mission systems if leak reaches equipment. | In Progress | CE Lighting
USSPC-FAC-2026-0073 | TRIRIGA-26-12073 | Peterson SFB | 210 | Operations Building 210 | SR-03 (Secure Server Room) | 2026-02-05 2105Z | USSPACECOM J2 | Urgent | HVAC | 2 | Excessive vibration noted on supply fan motor; bearing noise audible. | Inspect fan motor bearings and replace if worn. | Yes – degrades mission operations center readiness. | Completed | CE HVAC | Technician responded and found Found seized bearing on supply fan. Replaced capacitor and verified compressor amp draw within spec. System tested and verified operational at 86°F. All work per UFC 3-410-01. | 2026-02-09
USSPC-FAC-2026-0074 | TRIRIGA-26-12074 | Schriever SFB | 400 | Satellite Operations Facility 400 | Antenna Maintenance Area | 2026-02-05 2205Z | USSPACECOM J3 | Preventive Maintenance | Fire Protection | 4 | Quarterly fire sprinkler system inspection due. | Inspect and restore fire suppression system functionality. | No – preventive maintenance. | In Progress | CE Fire Protection
USSPC-FAC-2026-0075 | TRIRIGA-26-12075 | Vandenberg SFB | 51 | Launch Operations Building 51 | Control Room | 2026-02-06 0220Z | USSPACECOM J4 | Urgent | HVAC | 2 | Refrigerant leak suspected on split system unit; ice formation on suction line. | Locate and repair refrigerant leak; recharge system to spec. | No – personnel safety concern. | Submitted | CE HVAC
USSPC-FAC-2026-0076 | TRIRIGA-26-12076 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-06 0315Z | USSPACECOM J6 | Urgent | Lighting | 2 | LED retrofit fixture failed prematurely; driver humming audible. | Replace failed LED driver and fixture. | Yes – degrades ground station equipment reliability. | Submitted | CE Lighting
USSPC-FAC-2026-0077 | TRIRIGA-26-12077 | Schriever SFB | 220 | Mission Support Building 220 | Electrical Closet | 2026-02-06 0335Z | USSPACECOM J4 | Urgent | Plumbing | 2 | Sewer odor present in restroom corridor; possible dry trap or vent issue. | Locate and correct source of sewer gas odor. | No – personnel safety concern. | Completed | CE Plumbing | Technician inspected and identified Found faulty mixing valve. Rebuilt backflow preventer with new internals; passed test. System pressure tested and verified at normal operating range. No further leaks observed. | 2026-02-09
USSPC-FAC-2026-0078 | TRIRIGA-26-12078 | Peterson SFB | 145 | Operations Building 145 | Conference Room 3 | 2026-02-06 0355Z | USSPACECOM J3 | Preventive Maintenance | Structural | 4 | Scheduled annual roof inspection and condition assessment. | Service overhead doors and dock leveler mechanisms. | No – preventive maintenance. | Approved | CE Structural
USSPC-FAC-2026-0079 | TRIRIGA-26-12079 | Peterson SFB | 210 | Operations Building 210 | UPS Room | 2026-02-06 0355Z | USSPACECOM J6 | Urgent | Fire Protection | 2 | Sprinkler system pressure gauge reading below minimum; 39 PSI observed. | Investigate low sprinkler pressure and restore to minimum. | Yes – supports space domain awareness operations. | In Progress | CE Fire Protection
USSPC-FAC-2026-0080 | TRIRIGA-26-12080 | Buckley SFB | 312 | Operations Annex 312 | Electrical Room | 2026-02-06 0420Z | USSPACECOM J6 | Urgent | Electrical | 3 | Arc flash indicators detected during routine thermographic scan of switchgear. | De-energize and inspect switchgear; address arc flash indicators. | No – quality of life issue; no mission degradation. | Approved | CE Electrical
USSPC-FAC-2026-0081 | TRIRIGA-26-12081 | Schriever SFB | 400 | Satellite Operations Facility 400 | Mechanical Room | 2026-02-06 0550Z | USSPACECOM J4 | Routine | HVAC | 3 | Return air temperature sensor reading erratic values; zone control degraded. | Replace return air temperature sensor and recalibrate. | Potential – could impact mission systems if leak reaches equipment. | Approved | CE HVAC
USSPC-FAC-2026-0082 | TRIRIGA-26-12082 | Vandenberg SFB | 134 | Range Control Facility 134 | Telemetry Room | 2026-02-06 0650Z | USSPACECOM J3 | Urgent | Plumbing | 3 | Domestic water pressure low throughout facility; measured at 31 PSI vs 60 PSI normal. | Investigate low water pressure and restore to normal. | No – aesthetic/comfort issue only. | Completed | CE Plumbing | Responded and isolated affected section. Identified water hammer from quick-closing valve. Rebuilt backflow preventer with new internals; passed test. Flow verified at all fixtures. Area cleaned and restored. | 2026-02-09
USSPC-FAC-2026-0083 | TRIRIGA-26-12083 | Schriever SFB | 400 | Satellite Operations Facility 400 | Ground Station Control Room | 2026-02-06 0715Z | USSPACECOM J2 | Urgent | Power Production | 2 | Generator exhaust leak detected at flexible coupling. | Repair exhaust leak and verify emissions containment. | No – personnel safety and usability concern. | Approved | CE Power Production
USSPC-FAC-2026-0084 | TRIRIGA-26-12084 | Buckley SFB | 312 | Operations Annex 312 | Rooftop | 2026-02-06 0750Z | USSPACECOM J3 | Routine | HVAC | 3 | Ductwork insulation degraded in mechanical chase; condensation dripping onto ceiling tiles. | Replace degraded duct insulation and remediate moisture. | No – personnel safety and usability concern. | Submitted | CE HVAC
USSPC-FAC-2026-0085 | TRIRIGA-26-12085 | Peterson SFB | 3 | Power Generation Facility 3 | Generator Bay 1 | 2026-02-06 1420Z | USSPACECOM J2 | Urgent | Lighting | 2 | Parking lot light pole 20 dark; ballast or photocell suspected. | Replace ballast or photocell and restore pole light operation. | Yes – impacts secure communications capability. | In Progress | CE Lighting
USSPC-FAC-2026-0086 | TRIRIGA-26-12086 | Schriever SFB | 220 | Mission Support Building 220 | Training Room | 2026-02-06 1510Z | USSPACECOM J3 | Emergency | Power Production | 2 | Fuel quality test results indicate water contamination in storage tank. | Drain contaminated fuel, polish tank, and resample. | Yes – affects classified processing environment. | In Progress | CE Power Production
USSPC-FAC-2026-0087 | TRIRIGA-26-12087 | Peterson SFB | 88 | Data Processing Facility 88 | Mechanical Room | 2026-02-06 1540Z | USSPACECOM J6 | Routine | Lighting | 4 | Flickering fluorescent fixtures in office area causing occupant complaints. | Replace flickering fixtures with new lamps or ballasts. | No – general facility maintenance. | Submitted | CE Lighting
USSPC-FAC-2026-0088 | TRIRIGA-26-12088 | Vandenberg SFB | 77 | Secure Data Facility 77 | Server Room A | 2026-02-06 1730Z | USSPACECOM J2 | Preventive Maintenance | Power Production | 4 | Quarterly fuel sampling and polishing service. | Investigate capacity loss and perform corrective maintenance. | No – preventive maintenance. | In Progress | CE Power Production
USSPC-FAC-2026-0089 | TRIRIGA-26-12089 | Vandenberg SFB | 134 | Range Control Facility 134 | Exterior HVAC Pad | 2026-02-06 1800Z | USSPACECOM J6 | Preventive Maintenance | HVAC | 4 | Seasonal changeover inspection required for heating/cooling systems. | Inspect, clean, and document AHU condition. | No – preventive maintenance. | Completed | CE HVAC | Inspected system per work order. Discovered failed economizer actuator. Replaced communication card and restored BAS integration. Verified airflow and temperature within acceptable parameters. Documentation submitted. | 2026-02-10
USSPC-FAC-2026-0090 | TRIRIGA-26-12090 | Peterson SFB | 105 | Communications Hub 105 | Ground Floor Lobby | 2026-02-06 1840Z | USSPACECOM J3 | Urgent | Electrical | 3 | Phase imbalance measured at 6% on main distribution panel. | Balance phase loading on main distribution panel. | Yes – supports satellite command and control systems. | In Progress | CE Electrical
USSPC-FAC-2026-0091 | TRIRIGA-26-12091 | Peterson SFB | 210 | Operations Building 210 | Ops Floor | 2026-02-06 1920Z | USSPACECOM J2 | Routine | Lighting | 4 | Flickering fluorescent fixtures in office area causing occupant complaints. | Replace flickering fixtures with new lamps or ballasts. | No – routine upkeep; no operational impact. | In Progress | CE Lighting
USSPC-FAC-2026-0092 | TRIRIGA-26-12092 | Schriever SFB | 155 | Operations Building 155 | Ops Floor | 2026-02-06 2240Z | USSPACECOM J4 | Urgent | Plumbing | 2 | Water hammer occurring in supply piping when fixtures cycle. | Install water hammer arrestors and secure piping supports. | No – routine upkeep; no operational impact. | Approved | CE Plumbing
USSPC-FAC-2026-0093 | TRIRIGA-26-12093 | Vandenberg SFB | 134 | Range Control Facility 134 | Generator Enclosure | 2026-02-07 0005Z | USSPACECOM J3 | Routine | Structural | 4 | Door frame misaligned; secure door not seating properly in frame. | Adjust or replace door frame hardware for proper operation. | No – routine upkeep; no operational impact. | Completed | CE Structural | Technician assessed condition and documented findings. Discovered freeze-thaw damage to concrete surface. Applied new sealant and verified weathertight condition. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-19
USSPC-FAC-2026-0094 | TRIRIGA-26-12094 | Peterson SFB | 145 | Operations Building 145 | Comm Closet | 2026-02-07 0055Z | USSPACECOM J3 | Urgent | HVAC | 2 | Intermittent fault on CRAC unit 6; temperature cycling outside acceptable range. | Troubleshoot CRAC unit fault and restore environmental controls. | Yes – supports satellite command and control systems. | Completed | CE HVAC | Technician responded and found Identified refrigerant undercharge due to slow leak at service valve. Replaced communication card and restored BAS integration. System tested and verified operational at 84°F. All work per UFC 3-410-01. | 2026-02-11
USSPC-FAC-2026-0095 | TRIRIGA-26-12095 | Peterson SFB | 88 | Data Processing Facility 88 | Mechanical Room | 2026-02-07 0530Z | USSPACECOM J4 | Emergency | Fire Protection | 1 | Sprinkler system pressure gauge reading below minimum; 38 PSI observed. | Investigate low sprinkler pressure and restore to minimum. | Yes – degrades ground station equipment reliability. | In Progress | CE Fire Protection
USSPC-FAC-2026-0096 | TRIRIGA-26-12096 | Schriever SFB | 400 | Satellite Operations Facility 400 | Server Room | 2026-02-07 0700Z | USSPACECOM J6 | Routine | Electrical | 3 | Conduit damage observed along exterior wall; wiring exposed to weather. | Repair conduit and reseal exterior penetration. | Potential – degradation may affect future mission readiness. | Completed | CE Electrical | Arrived on-site, performed lockout/tagout, and investigated. Found loose connection at breaker lug causing arcing. Re-terminated connection with proper torque and applied anti-oxidant. All circuits tested and verified. Arc flash labels updated. | 2026-02-25
USSPC-FAC-2026-0097 | TRIRIGA-26-12097 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-07 0850Z | USSPACECOM J6 | Emergency | Structural | 1 | Roof membrane damage identified during routine walk-down; ponding water present. | Repair roof membrane and address ponding condition. | Yes – impacts secure communications capability. | In Progress | CE Structural
USSPC-FAC-2026-0098 | TRIRIGA-26-12098 | Vandenberg SFB | 51 | Launch Operations Building 51 | Equipment Room | 2026-02-07 0930Z | USSPACECOM J6 | Routine | Plumbing | 3 | Corrosion visible on exposed copper piping in mechanical chase. | Evaluate pipe corrosion and replace affected sections. | No – general facility maintenance. | Submitted | CE Plumbing
USSPC-FAC-2026-0099 | TRIRIGA-26-12099 | Buckley SFB | 180 | Mission Support Facility 180 | Equipment Room A | 2026-02-07 1145Z | USSPACECOM J6 | Urgent | Power Production | 3 | Fuel quality test results indicate water contamination in storage tank. | Drain contaminated fuel, polish tank, and resample. | Yes – affects classified processing environment. | In Progress | CE Power Production
USSPC-FAC-2026-0100 | TRIRIGA-26-12100 | Vandenberg SFB | 51 | Launch Operations Building 51 | Electrical Room | 2026-02-07 1300Z | USSPACECOM J2 | Emergency | Electrical | 2 | Voltage sag measured at distribution panel; equipment brownouts reported. | Investigate voltage sag source and correct distribution issue. | Yes – affects classified processing environment. | In Progress | CE Electrical
USSPC-FAC-2026-0101 | TRIRIGA-26-12101 | Schriever SFB | 220 | Mission Support Building 220 | Corridor B | 2026-02-07 1645Z | USSPACECOM J6 | Routine | Power Production | 4 | Automatic transfer switch not sensing utility power loss correctly. | Troubleshoot ATS sensing circuit and restore proper operation. | Potential – risk to nearby equipment if condition worsens. | Approved | CE Power Production
USSPC-FAC-2026-0102 | TRIRIGA-26-12102 | Schriever SFB | 400 | Satellite Operations Facility 400 | Server Room | 2026-02-07 1710Z | USSPACECOM J6 | Emergency | Plumbing | 2 | Condensate drain line from AHU clogged; water collecting in drain pan. | Clear condensate drain line and treat to prevent recurrence. | Yes – degrades ground station equipment reliability. | In Progress | CE Plumbing
USSPC-FAC-2026-0103 | TRIRIGA-26-12103 | Peterson SFB | 145 | Operations Building 145 | Break Room | 2026-02-07 1955Z | USSPACECOM J3 | Emergency | Electrical | 1 | Electrical panel cover missing fasteners; exposed energized components. | Secure panel cover and replace missing fasteners. | Yes – mission-critical data processing environment. | Completed | CE Electrical | Arrived on-site, performed lockout/tagout, and investigated. Discovered failed UPS battery cells in string 2. Replaced damaged conductor section and resealed conduit. All circuits tested and verified. Arc flash labels updated. | 2026-02-09
USSPC-FAC-2026-0104 | TRIRIGA-26-12104 | Schriever SFB | 400 | Satellite Operations Facility 400 | Antenna Maintenance Area | 2026-02-07 2105Z | USSPACECOM J3 | Routine | Structural | 3 | Expansion joint sealant deteriorated on exterior wall; gap visible. | Remove and replace expansion joint sealant. | No – personnel safety and usability concern. | Completed | CE Structural | Technician assessed condition and documented findings. Identified worn hinge pins on door frame. Applied membrane patch and verified watertight seal. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-23
USSPC-FAC-2026-0105 | TRIRIGA-26-12105 | Schriever SFB | 220 | Mission Support Building 220 | Lobby | 2026-02-07 2145Z | USSPACECOM J4 | Routine | Lighting | 4 | Exterior security lighting inoperative on building north side. | Repair exterior security lighting and verify coverage. | No – personnel safety concern. | Submitted | CE Lighting
USSPC-FAC-2026-0106 | TRIRIGA-26-12106 | Peterson SFB | 105 | Communications Hub 105 | HVAC Plenum | 2026-02-08 0020Z | USSPACECOM J3 | Urgent | Lighting | 2 | LED retrofit fixture failed prematurely; driver humming audible. | Replace failed LED driver and fixture. | Potential – degradation may affect future mission readiness. | In Progress | CE Lighting
USSPC-FAC-2026-0107 | TRIRIGA-26-12107 | Vandenberg SFB | 51 | Launch Operations Building 51 | Roof | 2026-02-08 0330Z | USSPACECOM J4 | Preventive Maintenance | Electrical | 4 | Scheduled thermographic survey of main electrical distribution. | Test UPS batteries and replace degraded cells. | No – preventive maintenance. | Completed | CE Electrical | Arrived on-site, performed lockout/tagout, and investigated. Found corroded neutral bus connection. Redistributed loads and labeled circuits per NEC 408.4. All circuits tested and verified. Arc flash labels updated. | 2026-02-21
USSPC-FAC-2026-0108 | TRIRIGA-26-12108 | Buckley SFB | 180 | Mission Support Facility 180 | Restroom Corridor | 2026-02-08 0440Z | USSPACECOM J2 | Urgent | Power Production | 2 | Fuel quality test results indicate water contamination in storage tank. | Drain contaminated fuel, polish tank, and resample. | No – quality of life issue; no mission degradation. | Completed | CE Power Production | Responded and performed diagnostic on power production equipment. Found block heater element open circuit. Replaced charger rectifier and verified float/equalize modes. Full load test passed; auto-start verified. Logbook updated. | 2026-02-11
USSPC-FAC-2026-0109 | TRIRIGA-26-12109 | Peterson SFB | 105 | Communications Hub 105 | HVAC Plenum | 2026-02-08 0545Z | USSPACECOM J3 | Routine | Plumbing | 3 | Water heater temperature/pressure relief valve discharging intermittently. | Inspect and repair T&P relief valve; verify operation. | No – administrative area; no mission systems affected. | In Progress | CE Plumbing
USSPC-FAC-2026-0110 | TRIRIGA-26-12110 | Vandenberg SFB | 77 | Secure Data Facility 77 | Battery Room | 2026-02-08 0600Z | USSPACECOM J6 | Routine | Lighting | 3 | High-bay lights in warehouse area cycling on and off intermittently. | Troubleshoot high-bay fixture cycling and correct. | Yes – affects missile warning operations continuity. | Completed | CE Lighting | Technician inspected lighting system. Found ballast failure in fluorescent fixture. Replaced photocell and verified dusk/dawn operation. All fixtures verified operational; light levels measured and within IES standards. | 2026-02-25
USSPC-FAC-2026-0111 | TRIRIGA-26-12111 | Peterson SFB | 88 | Data Processing Facility 88 | Battery Room | 2026-02-08 0610Z | USSPACECOM J2 | Emergency | Lighting | 2 | Flickering fluorescent fixtures in office area causing occupant complaints. | Replace flickering fixtures with new lamps or ballasts. | Yes – impacts secure communications capability. | In Progress | CE Lighting
USSPC-FAC-2026-0112 | TRIRIGA-26-12112 | Vandenberg SFB | 77 | Secure Data Facility 77 | Server Room A | 2026-02-08 0750Z | USSPACECOM J2 | Emergency | Plumbing | 2 | Sewer odor present in restroom corridor; possible dry trap or vent issue. | Locate and correct source of sewer gas odor. | Yes – supports space domain awareness operations. | Approved | CE Plumbing
USSPC-FAC-2026-0113 | TRIRIGA-26-12113 | Peterson SFB | 3 | Power Generation Facility 3 | Fuel Storage Area | 2026-02-08 0855Z | USSPACECOM J3 | Urgent | Power Production | 2 | Automatic transfer switch not sensing utility power loss correctly. | Troubleshoot ATS sensing circuit and restore proper operation. | Yes – loss of backup power to mission facilities. | Completed | CE Power Production | Technician inspected generator and support systems. Found low coolant level from radiator seep. Replaced charger rectifier and verified float/equalize modes. Generator started, loaded, and verified at rated output. Transfer tested successfully. | 2026-02-10
USSPC-FAC-2026-0114 | TRIRIGA-26-12114 | Buckley SFB | 180 | Mission Support Facility 180 | Exterior Pad | 2026-02-08 0955Z | USSPACECOM J2 | Urgent | Plumbing | 3 | Corrosion visible on exposed copper piping in mechanical chase. | Evaluate pipe corrosion and replace affected sections. | No – aesthetic/comfort issue only. | Submitted | CE Plumbing
USSPC-FAC-2026-0115 | TRIRIGA-26-12115 | Peterson SFB | 3 | Power Generation Facility 3 | Transfer Switch Room | 2026-02-08 1520Z | USSPACECOM J6 | Preventive Maintenance | Fire Protection | 4 | Fire extinguisher annual inspection and certification. | Schedule and perform FM-200 system annual inspection. | No – preventive maintenance. | Scheduled | CE Fire Protection
USSPC-FAC-2026-0116 | TRIRIGA-26-12116 | Vandenberg SFB | 77 | Secure Data Facility 77 | Battery Room | 2026-02-08 1605Z | USSPACECOM J3 | Routine | HVAC | 3 | Ductwork insulation degraded in mechanical chase; condensation dripping onto ceiling tiles. | Replace degraded duct insulation and remediate moisture. | Yes – supports satellite uplink equipment. | Completed | CE HVAC | Inspected system per work order. Found seized bearing on supply fan. Replaced bearing assembly and balanced fan. Verified airflow and temperature within acceptable parameters. Documentation submitted. | 2026-02-11
USSPC-FAC-2026-0117 | TRIRIGA-26-12117 | Buckley SFB | 180 | Mission Support Facility 180 | Exterior Pad | 2026-02-08 1705Z | USSPACECOM J2 | Routine | HVAC | 3 | Condensate overflow detected at air handling unit; water pooling on mechanical room floor. | Clear condensate drain and inspect for root cause of overflow. | Yes – degrades ground station equipment reliability. | Approved | CE HVAC
USSPC-FAC-2026-0118 | TRIRIGA-26-12118 | Peterson SFB | 88 | Data Processing Facility 88 | Receiving Area | 2026-02-08 1740Z | USSPACECOM J6 | Urgent | HVAC | 2 | Return air temperature sensor reading erratic values; zone control degraded. | Replace return air temperature sensor and recalibrate. | Yes – impacts launch operations support systems. | In Progress | CE HVAC
USSPC-FAC-2026-0119 | TRIRIGA-26-12119 | Vandenberg SFB | 77 | Secure Data Facility 77 | Electrical Vault | 2026-02-08 1850Z | USSPACECOM J6 | Urgent | Power Production | 2 | Generator exhaust leak detected at flexible coupling. | Repair exhaust leak and verify emissions containment. | Yes – supports satellite uplink equipment. | In Progress | CE Power Production
USSPC-FAC-2026-0120 | TRIRIGA-26-12120 | Peterson SFB | 105 | Communications Hub 105 | Ground Floor Lobby | 2026-02-08 2005Z | USSPACECOM J3 | Emergency | HVAC | 2 | Exhaust fan inoperative in mechanical room; ambient temperature elevated. | Repair or replace exhaust fan motor. | Yes – affects continuous space surveillance mission. | Completed | CE HVAC | Technician responded and found Discovered failed VFD drive board. Replaced bearing assembly and balanced fan. System tested and verified operational at 95°F. All work per UFC 3-410-01. | 2026-02-08
USSPC-FAC-2026-0121 | TRIRIGA-26-12121 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-08 2020Z | USSPACECOM J2 | Urgent | Electrical | 2 | Arc flash indicators detected during routine thermographic scan of switchgear. | De-energize and inspect switchgear; address arc flash indicators. | Yes – loss of backup power to mission facilities. | Submitted | CE Electrical
USSPC-FAC-2026-0122 | TRIRIGA-26-12122 | Schriever SFB | 400 | Satellite Operations Facility 400 | Ground Station Control Room | 2026-02-08 2115Z | USSPACECOM J3 | Urgent | HVAC | 3 | Degraded airflow detected in underfloor plenum; hot spots forming near rack rows. | Investigate underfloor airflow restriction and restore cooling distribution. | Yes – supports satellite command and control systems. | Approved | CE HVAC
USSPC-FAC-2026-0123 | TRIRIGA-26-12123 | Schriever SFB | 155 | Operations Building 155 | Watch Floor | 2026-02-09 0020Z | USSPACECOM J6 | Emergency | Electrical | 1 | Conduit damage observed along exterior wall; wiring exposed to weather. | Repair conduit and reseal exterior penetration. | Yes – affects classified processing environment. | Completed | CE Electrical | Arrived on-site, performed lockout/tagout, and investigated. Identified undersized conductor on overloaded circuit. Cleaned and re-torqued neutral bus connections. All circuits tested and verified. Arc flash labels updated. | 2026-02-11
USSPC-FAC-2026-0124 | TRIRIGA-26-12124 | Peterson SFB | 145 | Operations Building 145 | Entry Vestibule | 2026-02-09 0105Z | USSPACECOM J3 | Routine | Electrical | 4 | Emergency power receptacle non-functional at designated location. | Repair or replace emergency power receptacle. | No – preventive maintenance. | Approved | CE Electrical
USSPC-FAC-2026-0125 | TRIRIGA-26-12125 | Schriever SFB | 155 | Operations Building 155 | UPS Room | 2026-02-09 0210Z | USSPACECOM J6 | Preventive Maintenance | Lighting | 4 | Preventive maintenance on exterior lighting and photocell replacement. | Perform 90-minute emergency lighting battery test and document. | No – preventive maintenance. | Scheduled | CE Lighting
USSPC-FAC-2026-0126 | TRIRIGA-26-12126 | Peterson SFB | 198 | Operations Building 198 | Corridor B | 2026-02-09 0245Z | USSPACECOM J3 | Preventive Maintenance | Fire Protection | 4 | Fire extinguisher annual inspection and certification. | Perform annual fire alarm inspection and testing. | No – preventive maintenance. | Completed | CE Fire Protection | Responded and placed system in test mode. Discovered failed fire alarm control module. Replaced pull station and tested alarm signal to panel. Fire alarm panel cleared; all devices verified operational. | 2026-02-27
USSPC-FAC-2026-0127 | TRIRIGA-26-12127 | Schriever SFB | 155 | Operations Building 155 | Mechanical Penthouse | 2026-02-09 0250Z | USSPACECOM J3 | Routine | Electrical | 3 | Ground fault detected on branch circuit serving critical equipment. | Locate and clear ground fault on branch circuit. | Yes – loss of backup power to mission facilities. | In Progress | CE Electrical
USSPC-FAC-2026-0128 | TRIRIGA-26-12128 | Schriever SFB | 400 | Satellite Operations Facility 400 | Electrical Room | 2026-02-09 0645Z | USSPACECOM J3 | Emergency | Plumbing | 1 | Domestic water pressure low throughout facility; measured at 26 PSI vs 60 PSI normal. | Investigate low water pressure and restore to normal. | Yes – affects continuous space surveillance mission. | In Progress | CE Plumbing
USSPC-FAC-2026-0129 | TRIRIGA-26-12129 | Peterson SFB | 3 | Power Generation Facility 3 | Fuel Storage Area | 2026-02-09 0700Z | USSPACECOM J6 | Emergency | Electrical | 2 | Overheating detected at bus bar connection in electrical room via thermal imaging. | Repair overheating connection and verify with thermal imaging. | Yes – impacts real-time telemetry processing. | Completed | CE Electrical | Arrived on-site, performed lockout/tagout, and investigated. Identified undersized conductor on overloaded circuit. Replaced conductor with properly sized wire per NEC. All circuits tested and verified. Arc flash labels updated. | 2026-02-11
USSPC-FAC-2026-0130 | TRIRIGA-26-12130 | Buckley SFB | 180 | Mission Support Facility 180 | Exterior Pad | 2026-02-09 0810Z | USSPACECOM J6 | Urgent | Structural | 3 | Crack observed in exterior wall exceeding 1/4 inch width; moisture intrusion suspected. | Assess crack, seal exterior, and monitor for propagation. | No – administrative area; no mission systems affected. | In Progress | CE Structural
USSPC-FAC-2026-0131 | TRIRIGA-26-12131 | Peterson SFB | 210 | Operations Building 210 | SR-01 (Primary Server Room) | 2026-02-09 0940Z | USSPACECOM J3 | Emergency | Lighting | 1 | Parking lot light pole 7 dark; ballast or photocell suspected. | Replace ballast or photocell and restore pole light operation. | Yes – impacts real-time telemetry processing. | In Progress | CE Lighting
USSPC-FAC-2026-0132 | TRIRIGA-26-12132 | Vandenberg SFB | 134 | Range Control Facility 134 | Mechanical Room | 2026-02-09 1250Z | USSPACECOM J6 | Preventive Maintenance | Lighting | 4 | Preventive maintenance on exterior lighting and photocell replacement. | Inspect and replace photocells on exterior fixtures. | No – preventive maintenance. | In Progress | CE Lighting
USSPC-FAC-2026-0133 | TRIRIGA-26-12133 | Peterson SFB | 88 | Data Processing Facility 88 | Receiving Area | 2026-02-09 1615Z | USSPACECOM J4 | Emergency | Lighting | 1 | Exit sign lamp out at emergency egress route. | Replace exit sign lamp and verify illumination. | Yes – supports satellite command and control systems. | Approved | CE Lighting
USSPC-FAC-2026-0134 | TRIRIGA-26-12134 | Schriever SFB | 155 | Operations Building 155 | Comm Closet 3A | 2026-02-09 1800Z | USSPACECOM J6 | Urgent | Electrical | 3 | Emergency power receptacle non-functional at designated location. | Repair or replace emergency power receptacle. | No – preventive maintenance. | Approved | CE Electrical
USSPC-FAC-2026-0135 | TRIRIGA-26-12135 | Buckley SFB | 180 | Mission Support Facility 180 | Restroom Corridor | 2026-02-09 1830Z | USSPACECOM J2 | Routine | Lighting | 3 | Exterior security lighting inoperative on building north side. | Repair exterior security lighting and verify coverage. | Potential – degradation may affect future mission readiness. | Completed | CE Lighting | Technician inspected lighting system. Discovered failed photocell. Repaired wiring connection and verified circuit integrity. All fixtures verified operational; light levels measured and within IES standards. | 2026-02-14
USSPC-FAC-2026-0136 | TRIRIGA-26-12136 | Peterson SFB | 145 | Operations Building 145 | Electrical Room | 2026-02-09 1920Z | USSPACECOM J4 | Routine | Electrical | 4 | Ground fault detected on branch circuit serving critical equipment. | Locate and clear ground fault on branch circuit. | No – general facility maintenance. | Submitted | CE Electrical
USSPC-FAC-2026-0137 | TRIRIGA-26-12137 | Peterson SFB | 88 | Data Processing Facility 88 | Server Hall A | 2026-02-09 1925Z | USSPACECOM J6 | Routine | Structural | 3 | Expansion joint sealant deteriorated on exterior wall; gap visible. | Remove and replace expansion joint sealant. | Yes – affects continuous space surveillance mission. | Completed | CE Structural | Arrived on-site and performed structural assessment. Found raised floor pedestal adjustment screws loosened. Patched spalled area with structural repair mortar. Condition stable; documented in facility records. | 2026-02-25
USSPC-FAC-2026-0138 | TRIRIGA-26-12138 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 2 | 2026-02-09 2110Z | USSPACECOM J4 | Preventive Maintenance | HVAC | 4 | Server room temperature measured at 90°F due to reduced airflow from AHU-8. | Inspect fan motor bearings and replace if worn. | No – preventive maintenance. | Completed | CE HVAC | Inspected system per work order. Identified refrigerant undercharge due to slow leak at service valve. Cleared drain, treated with biocide, and verified flow. Verified airflow and temperature within acceptable parameters. Documentation submitted. | 2026-02-12
USSPC-FAC-2026-0139 | TRIRIGA-26-12139 | Peterson SFB | 88 | Data Processing Facility 88 | Server Hall B | 2026-02-09 2210Z | USSPACECOM J3 | Urgent | ESS | 3 | Electronic lock on secure door not responding to valid credentials. | Replace electronic lock actuator and verify operation. | No – personnel safety concern. | Approved | CE ESS
USSPC-FAC-2026-0140 | TRIRIGA-26-12140 | Peterson SFB | 88 | Data Processing Facility 88 | Receiving Area | 2026-02-09 2215Z | USSPACECOM J3 | Routine | Plumbing | 3 | Sewer odor present in restroom corridor; possible dry trap or vent issue. | Locate and correct source of sewer gas odor. | Yes – intermittent loss of operator consoles. | Completed | CE Plumbing | Responded and isolated affected section. Identified water hammer from quick-closing valve. Rebuilt backflow preventer with new internals; passed test. Flow verified at all fixtures. Area cleaned and restored. | 2026-02-22
USSPC-FAC-2026-0141 | TRIRIGA-26-12141 | Schriever SFB | 155 | Operations Building 155 | Comm Closet 3A | 2026-02-09 2330Z | USSPACECOM J3 | Urgent | HVAC | 2 | Exhaust fan inoperative in mechanical room; ambient temperature elevated. | Repair or replace exhaust fan motor. | Yes – supports satellite command and control systems. | Completed | CE HVAC | Inspected system per work order. Found clogged condensate drain line. Replaced actuator and verified damper full-stroke operation. Verified airflow and temperature within acceptable parameters. Documentation submitted. | 2026-02-13
USSPC-FAC-2026-0142 | TRIRIGA-26-12142 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-10 0000Z | USSPACECOM J3 | Routine | Electrical | 3 | Overheating detected at bus bar connection in electrical room via thermal imaging. | Repair overheating connection and verify with thermal imaging. | Yes – affects classified processing environment. | Submitted | CE Electrical
USSPC-FAC-2026-0143 | TRIRIGA-26-12143 | Buckley SFB | 312 | Operations Annex 312 | Secure Entry Vestibule | 2026-02-10 0020Z | USSPACECOM J3 | Emergency | Electrical | 2 | Power monitoring system reporting harmonics above threshold on critical bus. | Install harmonic filtering or identify harmonic source. | Yes – impacts real-time telemetry processing. | Approved | CE Electrical
USSPC-FAC-2026-0144 | TRIRIGA-26-12144 | Buckley SFB | 312 | Operations Annex 312 | Rooftop | 2026-02-10 0040Z | USSPACECOM J6 | Urgent | ESS | 2 | Access control panel communication fault; door status unknown. | Restore communication between access control panel and host. | Yes – affects continuous space surveillance mission. | Approved | CE ESS
USSPC-FAC-2026-0145 | TRIRIGA-26-12145 | Vandenberg SFB | 51 | Launch Operations Building 51 | Roof | 2026-02-10 0135Z | USSPACECOM J2 | Routine | HVAC | 4 | Building automation system reporting communication loss with AHU-5 controller. | Restore BAS communication with AHU controller. | No – personnel safety and usability concern. | In Progress | CE HVAC
USSPC-FAC-2026-0146 | TRIRIGA-26-12146 | Schriever SFB | 400 | Satellite Operations Facility 400 | Electrical Room | 2026-02-10 0235Z | USSPACECOM J4 | Preventive Maintenance | ESS | 4 | Preventive maintenance on access control system firmware and hardware. | Repair intercom system and test two-way communication. | No – preventive maintenance. | Scheduled | CE ESS
USSPC-FAC-2026-0147 | TRIRIGA-26-12147 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-10 0310Z | USSPACECOM J6 | Routine | Lighting | 4 | Emergency lighting battery unit failed self-test; no backup illumination. | Replace emergency lighting battery unit and test. | No – quality of life issue; no mission degradation. | Completed | CE Lighting | Technician inspected lighting system. Discovered failed photocell. Replaced ballast and installed new lamps. All fixtures verified operational; light levels measured and within IES standards. | 2026-02-23
USSPC-FAC-2026-0148 | TRIRIGA-26-12148 | Buckley SFB | 312 | Operations Annex 312 | Mechanical Room | 2026-02-10 0405Z | USSPACECOM J6 | Urgent | HVAC | 3 | Excessive vibration noted on supply fan motor; bearing noise audible. | Inspect fan motor bearings and replace if worn. | Yes – impacts launch operations support systems. | Completed | CE HVAC | Inspected system per work order. Found dirty evaporator coil restricting airflow. Replaced communication card and restored BAS integration. Verified airflow and temperature within acceptable parameters. Documentation submitted. | 2026-02-11
USSPC-FAC-2026-0149 | TRIRIGA-26-12149 | Peterson SFB | 105 | Communications Hub 105 | HVAC Plenum | 2026-02-10 0405Z | USSPACECOM J4 | Emergency | Fire Protection | 2 | Clean agent suppression system showing low bottle pressure. | Recharge or replace clean agent suppression bottles. | Yes – affects classified processing environment. | Approved | CE Fire Protection
USSPC-FAC-2026-0150 | TRIRIGA-26-12150 | Peterson SFB | 210 | Operations Building 210 | Ops Floor | 2026-02-10 0435Z | USSPACECOM J3 | Emergency | Electrical | 1 | PDU in server room reporting overload alarm on Phase B. | Investigate PDU overload and redistribute loads as needed. | Yes – loss of backup power to mission facilities. | In Progress | CE Electrical
USSPC-FAC-2026-0151 | TRIRIGA-26-12151 | Buckley SFB | 180 | Mission Support Facility 180 | Restroom Corridor | 2026-02-10 0620Z | USSPACECOM J3 | Urgent | HVAC | 3 | Cooling unit shut down unexpectedly; room temperature rising steadily. | Restore HVAC operation and verify system stability. | Yes – impacts launch operations support systems. | In Progress | CE HVAC
USSPC-FAC-2026-0152 | TRIRIGA-26-12152 | Peterson SFB | 105 | Communications Hub 105 | HVAC Plenum | 2026-02-10 0730Z | USSPACECOM J6 | Emergency | ESS | 1 | Motion sensor PIR detector degraded; detection range reduced. | Replace PIR motion sensor and verify detection coverage. | Yes – delayed access to mission operations spaces. | Completed | CE ESS | Responded and coordinated with security forces. Identified network cable fault to camera. Replaced lock solenoid and tested with valid credentials. Credentials tested at affected entry points; full functionality confirmed. | 2026-02-12
USSPC-FAC-2026-0153 | TRIRIGA-26-12153 | Buckley SFB | 180 | Mission Support Facility 180 | Mechanical Room | 2026-02-10 0755Z | USSPACECOM J6 | Routine | ESS | 3 | Access control panel communication fault; door status unknown. | Restore communication between access control panel and host. | Yes – degrades ground station equipment reliability. | Approved | CE ESS
USSPC-FAC-2026-0154 | TRIRIGA-26-12154 | Peterson SFB | 210 | Operations Building 210 | Ops Floor | 2026-02-10 0800Z | USSPACECOM J6 | Emergency | Electrical | 2 | Intermittent power loss to operator consoles on ops floor. | Troubleshoot intermittent power issue and restore stable supply. | Yes – affects classified processing environment. | Approved | CE Electrical
USSPC-FAC-2026-0155 | TRIRIGA-26-12155 | Schriever SFB | 400 | Satellite Operations Facility 400 | Ground Station Control Room | 2026-02-10 0805Z | USSPACECOM J3 | Emergency | ESS | 2 | Electronic lock on secure door not responding to valid credentials. | Replace electronic lock actuator and verify operation. | Yes – supports space domain awareness operations. | Completed | CE ESS | Technician inspected ESS components. Identified controller firmware communication error. Cleaned sensor lens and recalibrated detection zone. System tested end-to-end; all access points verified operational. Security notified of restoration. | 2026-02-12
USSPC-FAC-2026-0156 | TRIRIGA-26-12156 | Peterson SFB | 145 | Operations Building 145 | Restroom Corridor | 2026-02-10 0840Z | USSPACECOM J6 | Urgent | Power Production | 3 | Fuel transfer pump inoperative; unable to refill day tank. | Repair or replace fuel transfer pump. | Yes – affects classified processing environment. | In Progress | CE Power Production
USSPC-FAC-2026-0157 | TRIRIGA-26-12157 | Buckley SFB | 312 | Operations Annex 312 | Electrical Room | 2026-02-10 1625Z | USSPACECOM J2 | Routine | HVAC | 3 | Ductwork insulation degraded in mechanical chase; condensation dripping onto ceiling tiles. | Replace degraded duct insulation and remediate moisture. | Potential – potential cascade failure if not addressed. | In Progress | CE HVAC
USSPC-FAC-2026-0158 | TRIRIGA-26-12158 | Vandenberg SFB | 77 | Secure Data Facility 77 | Mechanical Room | 2026-02-10 2150Z | USSPACECOM J6 | Emergency | Plumbing | 2 | Floor drain backing up intermittently in mechanical room. | Clear floor drain blockage and verify flow. | Yes – mission-critical data processing environment. | Completed | CE Plumbing | Responded and isolated affected section. Identified failed pressure regulator. Replaced pressure regulator and set to 55 PSI. Flow verified at all fixtures. Area cleaned and restored. | 2026-02-11
USSPC-FAC-2026-0159 | TRIRIGA-26-12159 | Vandenberg SFB | 134 | Range Control Facility 134 | Mechanical Room | 2026-02-10 2235Z | USSPACECOM J2 | Routine | Plumbing | 3 | Hot water temperature at fixtures below acceptable range; measured 94°F. | Diagnose hot water temperature issue and adjust or repair. | Yes – affects missile warning operations continuity. | Approved | CE Plumbing
USSPC-FAC-2026-0160 | TRIRIGA-26-12160 | Vandenberg SFB | 51 | Launch Operations Building 51 | Control Room | 2026-02-10 2305Z | USSPACECOM J3 | Urgent | Power Production | 3 | Generator coolant temperature alarm during loaded run test. | Diagnose cooling system alarm and restore normal operation. | No – routine upkeep; no operational impact. | Submitted | CE Power Production
USSPC-FAC-2026-0161 | TRIRIGA-26-12161 | Schriever SFB | 220 | Mission Support Building 220 | Corridor B | 2026-02-11 0025Z | USSPACECOM J4 | Preventive Maintenance | HVAC | 4 | Scheduled quarterly inspection of air handling units. | Clear condensate drain and inspect for root cause of overflow. | No – preventive maintenance. | Approved | CE HVAC
USSPC-FAC-2026-0162 | TRIRIGA-26-12162 | Peterson SFB | 88 | Data Processing Facility 88 | Server Hall B | 2026-02-11 0105Z | USSPACECOM J4 | Routine | HVAC | 4 | Supply air temperature out of tolerance; measured 78°F against 72°F setpoint. | Diagnose and correct supply air temperature deviation. | No – preventive maintenance. | In Progress | CE HVAC
USSPC-FAC-2026-0163 | TRIRIGA-26-12163 | Buckley SFB | 180 | Mission Support Facility 180 | Restroom Corridor | 2026-02-11 0220Z | USSPACECOM J6 | Emergency | ESS | 1 | Perimeter fence detection system reporting intermittent faults. | Troubleshoot perimeter detection system and restore monitoring. | Yes – delayed access to mission operations spaces. | Approved | CE ESS
USSPC-FAC-2026-0164 | TRIRIGA-26-12164 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-11 0220Z | USSPACECOM J2 | Urgent | Electrical | 2 | Intermittent power loss to operator consoles on ops floor. | Troubleshoot intermittent power issue and restore stable supply. | Yes – loss of backup power to mission facilities. | Completed | CE Electrical | Responded to work order. Found loose connection at breaker lug causing arcing. Redistributed loads and labeled circuits per NEC 408.4. Thermal scan confirmed normal temperatures. Completed per NEC requirements. | 2026-02-13
USSPC-FAC-2026-0165 | TRIRIGA-26-12165 | Peterson SFB | 42 | Administrative Building 42 | Janitor Closet | 2026-02-11 0240Z | USSPACECOM J2 | Routine | ESS | 3 | Motion sensor PIR detector degraded; detection range reduced. | Replace PIR motion sensor and verify detection coverage. | Yes – impacts launch operations support systems. | Approved | CE ESS
USSPC-FAC-2026-0166 | TRIRIGA-26-12166 | Schriever SFB | 155 | Operations Building 155 | Watch Floor | 2026-02-11 0340Z | USSPACECOM J4 | Routine | Plumbing | 4 | Minor water leak observed on chilled water return line. | Repair leaking pipe section and verify system pressure. | No – personnel safety and usability concern. | Submitted | CE Plumbing
USSPC-FAC-2026-0167 | TRIRIGA-26-12167 | Schriever SFB | 400 | Satellite Operations Facility 400 | Server Room | 2026-02-11 0440Z | USSPACECOM J6 | Urgent | Lighting | 3 | Emergency lighting battery unit failed self-test; no backup illumination. | Replace emergency lighting battery unit and test. | Potential – potential cascade failure if not addressed. | Approved | CE Lighting
USSPC-FAC-2026-0168 | TRIRIGA-26-12168 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-11 0530Z | USSPACECOM J6 | Urgent | HVAC | 3 | Condensate overflow detected at air handling unit; water pooling on mechanical room floor. | Clear condensate drain and inspect for root cause of overflow. | No – aesthetic/comfort issue only. | Approved | CE HVAC
USSPC-FAC-2026-0169 | TRIRIGA-26-12169 | Vandenberg SFB | 134 | Range Control Facility 134 | Exterior HVAC Pad | 2026-02-11 0550Z | USSPACECOM J3 | Routine | HVAC | 4 | Supply air temperature out of tolerance; measured 80°F against 71°F setpoint. | Diagnose and correct supply air temperature deviation. | No – administrative area; no mission systems affected. | Submitted | CE HVAC
USSPC-FAC-2026-0170 | TRIRIGA-26-12170 | Buckley SFB | 312 | Operations Annex 312 | Rooftop | 2026-02-11 0625Z | USSPACECOM J3 | Routine | Electrical | 4 | UPS system reporting degraded battery capacity; estimated runtime below threshold. | Test UPS batteries and replace degraded cells. | No – administrative area; no mission systems affected. | Approved | CE Electrical
USSPC-FAC-2026-0171 | TRIRIGA-26-12171 | Schriever SFB | 400 | Satellite Operations Facility 400 | Mechanical Room | 2026-02-11 0800Z | USSPACECOM J3 | Urgent | Electrical | 3 | Conduit damage observed along exterior wall; wiring exposed to weather. | Repair conduit and reseal exterior penetration. | No – preventive maintenance. | Approved | CE Electrical
USSPC-FAC-2026-0172 | TRIRIGA-26-12172 | Schriever SFB | 220 | Mission Support Building 220 | Lobby | 2026-02-11 0900Z | USSPACECOM J3 | Emergency | HVAC | 1 | Ductwork insulation degraded in mechanical chase; condensation dripping onto ceiling tiles. | Replace degraded duct insulation and remediate moisture. | Yes – supports space domain awareness operations. | Approved | CE HVAC
USSPC-FAC-2026-0173 | TRIRIGA-26-12173 | Peterson SFB | 210 | Operations Building 210 | SR-03 (Secure Server Room) | 2026-02-11 1455Z | USSPACECOM J2 | Emergency | HVAC | 1 | Supply air temperature out of tolerance; measured 90°F against 72°F setpoint. | Diagnose and correct supply air temperature deviation. | Yes – loss of backup power to mission facilities. | In Progress | CE HVAC
USSPC-FAC-2026-0174 | TRIRIGA-26-12174 | Peterson SFB | 105 | Communications Hub 105 | Ground Floor Lobby | 2026-02-11 1610Z | USSPACECOM J4 | Urgent | Fire Protection | 3 | Fire suppression control panel reporting system fault. | Inspect and restore fire suppression system functionality. | Yes – delayed access to mission operations spaces. | Approved | CE Fire Protection
USSPC-FAC-2026-0175 | TRIRIGA-26-12175 | Vandenberg SFB | 134 | Range Control Facility 134 | Ops Floor | 2026-02-11 1655Z | USSPACECOM J4 | Routine | Structural | 4 | Raised floor panels loose near network racks. | Secure panels and ensure floor stability. | No – administrative area; no mission systems affected. | Completed | CE Structural | Technician assessed condition and documented findings. Found deteriorated roof membrane at flashing detail. Applied new sealant and verified weathertight condition. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-16
USSPC-FAC-2026-0176 | TRIRIGA-26-12176 | Schriever SFB | 155 | Operations Building 155 | Mechanical Penthouse | 2026-02-11 1700Z | USSPACECOM J6 | Urgent | Electrical | 3 | Phase imbalance measured at 9% on main distribution panel. | Balance phase loading on main distribution panel. | Yes – affects classified processing environment. | Completed | CE Electrical | Technician de-energized and inspected per NFPA 70E. Discovered failed UPS battery cells in string 2. Replaced damaged conductor section and resealed conduit. System re-energized and tested under load; operating normally. | 2026-02-13
USSPC-FAC-2026-0177 | TRIRIGA-26-12177 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 2 | 2026-02-11 1745Z | USSPACECOM J4 | Routine | Electrical | 4 | UPS system reporting degraded battery capacity; estimated runtime below threshold. | Test UPS batteries and replace degraded cells. | No – administrative area; no mission systems affected. | Approved | CE Electrical
USSPC-FAC-2026-0178 | TRIRIGA-26-12178 | Schriever SFB | 155 | Operations Building 155 | Mechanical Penthouse | 2026-02-11 1755Z | USSPACECOM J2 | Emergency | Structural | 2 | Retaining wall showing lateral displacement; drainage weeps clogged. | Clear retaining wall weeps and assess lateral stability. | Yes – intermittent loss of operator consoles. | Completed | CE Structural | Technician assessed condition and documented findings. Discovered freeze-thaw damage to concrete surface. Patched spalled area with structural repair mortar. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-13
USSPC-FAC-2026-0179 | TRIRIGA-26-12179 | Schriever SFB | 400 | Satellite Operations Facility 400 | Mechanical Room | 2026-02-11 1830Z | USSPACECOM J2 | Preventive Maintenance | HVAC | 4 | Annual filter replacement and coil cleaning for AHU-8 through AHU-5. | Perform seasonal changeover inspection and adjustments. | No – preventive maintenance. | Completed | CE HVAC | Arrived on-site, isolated unit, and performed diagnostic. Identified refrigerant undercharge due to slow leak at service valve. Replaced capacitor and verified compressor amp draw within spec. Post-repair monitoring confirmed stable operation. | 2026-02-22
USSPC-FAC-2026-0180 | TRIRIGA-26-12180 | Schriever SFB | 220 | Mission Support Building 220 | Training Room | 2026-02-11 1835Z | USSPACECOM J3 | Urgent | Lighting | 3 | Exterior security lighting inoperative on building north side. | Repair exterior security lighting and verify coverage. | Yes – affects classified processing environment. | Approved | CE Lighting
USSPC-FAC-2026-0181 | TRIRIGA-26-12181 | Peterson SFB | 88 | Data Processing Facility 88 | Chiller Plant | 2026-02-11 1850Z | USSPACECOM J3 | Urgent | HVAC | 2 | Cooling tower fan motor tripped on overload; condenser water temperature rising. | Repair cooling tower fan motor and test operation. | Yes – supports satellite uplink equipment. | In Progress | CE HVAC
USSPC-FAC-2026-0182 | TRIRIGA-26-12182 | Buckley SFB | 180 | Mission Support Facility 180 | Electrical Room | 2026-02-11 2030Z | USSPACECOM J4 | Routine | HVAC | 4 | Ductwork insulation degraded in mechanical chase; condensation dripping onto ceiling tiles. | Replace degraded duct insulation and remediate moisture. | No – routine upkeep; no operational impact. | In Progress | CE HVAC
USSPC-FAC-2026-0183 | TRIRIGA-26-12183 | Vandenberg SFB | 77 | Secure Data Facility 77 | Server Room B | 2026-02-12 0135Z | USSPACECOM J2 | Urgent | Structural | 2 | Roof membrane damage identified during routine walk-down; ponding water present. | Repair roof membrane and address ponding condition. | No – personnel safety concern. | Submitted | CE Structural
USSPC-FAC-2026-0184 | TRIRIGA-26-12184 | Schriever SFB | 400 | Satellite Operations Facility 400 | Mechanical Room | 2026-02-12 0720Z | USSPACECOM J2 | Urgent | HVAC | 3 | Building automation system reporting communication loss with AHU-2 controller. | Restore BAS communication with AHU controller. | Potential – could impact mission systems if leak reaches equipment. | In Progress | CE HVAC
USSPC-FAC-2026-0185 | TRIRIGA-26-12185 | Schriever SFB | 302 | Communications Facility 302 | Equipment Room 1 | 2026-02-12 1200Z | USSPACECOM J6 | Emergency | Plumbing | 1 | Hot water temperature at fixtures below acceptable range; measured 83°F. | Diagnose hot water temperature issue and adjust or repair. | Yes – intermittent loss of operator consoles. | Completed | CE Plumbing | Responded and isolated affected section. Found faulty mixing valve. Replaced mixing valve and set to 120°F output. Flow verified at all fixtures. Area cleaned and restored. | 2026-02-12
USSPC-FAC-2026-0186 | TRIRIGA-26-12186 | Peterson SFB | 198 | Operations Building 198 | Lobby | 2026-02-12 1205Z | USSPACECOM J3 | Routine | Fire Protection | 4 | Fire alarm pull station damaged at egress point; device non-functional. | Replace damaged fire alarm pull station. | Potential – could impact mission systems if leak reaches equipment. | Submitted | CE Fire Protection
USSPC-FAC-2026-0187 | TRIRIGA-26-12187 | Peterson SFB | 88 | Data Processing Facility 88 | Server Hall A | 2026-02-12 1215Z | USSPACECOM J2 | Emergency | Structural | 2 | Raised floor panels loose near network racks. | Secure panels and ensure floor stability. | Yes – impacts launch operations support systems. | Completed | CE Structural | Technician assessed condition and documented findings. Identified worn hinge pins on door frame. Patched spalled area with structural repair mortar. Area safe for occupancy. Follow-up inspection scheduled if required. | 2026-02-12
USSPC-FAC-2026-0188 | TRIRIGA-26-12188 | Peterson SFB | 3 | Power Generation Facility 3 | Transfer Switch Room | 2026-02-12 1430Z | USSPACECOM J3 | Routine | Structural | 4 | Expansion joint sealant deteriorated on exterior wall; gap visible. | Remove and replace expansion joint sealant. | No – routine upkeep; no operational impact. | Completed | CE Structural | Arrived on-site and performed structural assessment. Identified moisture intrusion through failed sealant. Patched spalled area with structural repair mortar. Condition stable; documented in facility records. | 2026-02-16
USSPC-FAC-2026-0189 | TRIRIGA-26-12189 | Peterson SFB | 145 | Operations Building 145 | Restroom Corridor | 2026-02-12 1455Z | USSPACECOM J6 | Preventive Maintenance | Power Production | 4 | Quarterly fuel sampling and polishing service. | Investigate capacity loss and perform corrective maintenance. | No – preventive maintenance. | Scheduled | CE Power Production
USSPC-FAC-2026-0190 | TRIRIGA-26-12190 | Peterson SFB | 145 | Operations Building 145 | Mechanical Room | 2026-02-12 1655Z | USSPACECOM J3 | Routine | Structural | 3 | Expansion joint sealant deteriorated on exterior wall; gap visible. | Remove and replace expansion joint sealant. | Yes – intermittent loss of operator consoles. | In Progress | CE Structural
USSPC-FAC-2026-0191 | TRIRIGA-26-12191 | Vandenberg SFB | 77 | Secure Data Facility 77 | Mechanical Room | 2026-02-12 1710Z | USSPACECOM J3 | Emergency | Fire Protection | 2 | Emergency exit sign non-illuminated in corridor section. | Replace emergency exit sign lamps and verify illumination. | Yes – supports satellite command and control systems. | Completed | CE Fire Protection | Responded and placed system in test mode. Found faulty smoke detector head. Replaced detector head and tested with canned smoke. Fire alarm panel cleared; all devices verified operational. | 2026-02-14
USSPC-FAC-2026-0192 | TRIRIGA-26-12192 | Peterson SFB | 88 | Data Processing Facility 88 | Receiving Area | 2026-02-12 1720Z | USSPACECOM J3 | Urgent | Fire Protection | 2 | Wet pipe sprinkler system showing signs of internal corrosion at test fitting. | Flush and test wet pipe sprinkler system. | Yes – intermittent loss of operator consoles. | Completed | CE Fire Protection | Technician inspected system per NFPA 72/25 requirements. Identified leaking sprinkler system check valve. Replaced detector head and tested with canned smoke. System placed back in service and tested. All zones normal. | 2026-02-16
USSPC-FAC-2026-0193 | TRIRIGA-26-12193 | Vandenberg SFB | 51 | Launch Operations Building 51 | Control Room | 2026-02-12 2325Z | USSPACECOM J6 | Routine | Fire Protection | 4 | Fire alarm pull station damaged at egress point; device non-functional. | Replace damaged fire alarm pull station. | No – personnel safety concern. | Completed | CE Fire Protection | Technician inspected system per NFPA 72/25 requirements. Found fire pump controller relay failure. Replaced pull station and tested alarm signal to panel. System placed back in service and tested. All zones normal. | 2026-02-24
USSPC-FAC-2026-0194 | TRIRIGA-26-12194 | Peterson SFB | 88 | Data Processing Facility 88 | Battery Room | 2026-02-13 0000Z | USSPACECOM J2 | Preventive Maintenance | Electrical | 4 | Preventive maintenance due on UPS battery string per manufacturer schedule. | Test and replace UPS batteries per maintenance schedule. | No – preventive maintenance. | Approved | CE Electrical
USSPC-FAC-2026-0195 | TRIRIGA-26-12195 | Peterson SFB | 145 | Operations Building 145 | Comm Closet | 2026-02-13 0320Z | USSPACECOM J3 | Emergency | HVAC | 1 | Return air temperature sensor reading erratic values; zone control degraded. | Replace return air temperature sensor and recalibrate. | Yes – supports satellite uplink equipment. | In Progress | CE HVAC
USSPC-FAC-2026-0196 | TRIRIGA-26-12196 | Buckley SFB | 312 | Operations Annex 312 | Mechanical Room | 2026-02-13 0435Z | USSPACECOM J3 | Routine | ESS | 4 | Intercom system non-functional at entry control point. | Repair intercom system and test two-way communication. | No – aesthetic/comfort issue only. | Approved | CE ESS
USSPC-FAC-2026-0197 | TRIRIGA-26-12197 | Peterson SFB | 105 | Communications Hub 105 | Antenna Equipment Room | 2026-02-13 0510Z | USSPACECOM J4 | Routine | Electrical | 3 | Conduit damage observed along exterior wall; wiring exposed to weather. | Repair conduit and reseal exterior penetration. | No – general facility maintenance. | Approved | CE Electrical
USSPC-FAC-2026-0198 | TRIRIGA-26-12198 | Peterson SFB | 88 | Data Processing Facility 88 | Electrical Vault | 2026-02-13 0615Z | USSPACECOM J6 | Routine | HVAC | 3 | Economizer damper stuck in closed position; outside air not being utilized. | Repair economizer damper actuator and verify operation. | Yes – degrades ground station equipment reliability. | In Progress | CE HVAC
USSPC-FAC-2026-0199 | TRIRIGA-26-12199 | Peterson SFB | 88 | Data Processing Facility 88 | Server Hall B | 2026-02-13 1220Z | USSPACECOM J3 | Urgent | Power Production | 3 | Automatic transfer switch not sensing utility power loss correctly. | Troubleshoot ATS sensing circuit and restore proper operation. | Yes – impacts secure communications capability. | In Progress | CE Power Production
USSPC-FAC-2026-0200 | TRIRIGA-26-12200 | Peterson SFB | 198 | Operations Building 198 | Loading Area | 2026-02-13 1245Z | USSPACECOM J6 | Preventive Maintenance | Plumbing | 4 | Scheduled backflow preventer testing and certification. | Inspect and repair T&P relief valve; verify operation. | No – preventive maintenance. | Completed | CE Plumbing | Responded and isolated affected section. Identified water hammer from quick-closing valve. Replaced mixing valve and set to 120°F output. Flow verified at all fixtures. Area cleaned and restored. | 2026-02-27